- Silver Creek Village WSC

- Emergency Response Plan For Public Drinking Water Utility Last Updated: April 2022

- ***REVIEW this Emergency Response Plan annually to make sure Emergency Contact Numbers and other information is accurate. Emergency Response Planning Template for Public Drinking Water Systems RCAP Regional Offices: If you need technical assistance to complete your Emergency Response Plan, please contact one of our regional offices listed below.

- Regional Offices 	Contact Number 	Web Address

- RCAP National Office 	888/321-7227 	www.rcap.org

- Western RCAP 		916/447-2854 	www.rcac.org

- Southeast RCAP 		866/928-3731 	www.southeastrcap.org

- Great Lakes RCAP 	800/775-9767 	www.glrcap.org

- Southern RCAP 		479/443-2700 	www.crg.org

- Northeast RCAP 		800/488-1969 	www.rcapsolutions.org

- Midwest RCAP 		952/758-4334 	www.map-inc.org

- This material is based upon work supported in part under a grant by the Rural Utilities Service, United States Department of Agriculture. Any opinions, findings, and conclusions or recommendations expressed in this material are solely the responsibility of the authors and do not necessarily represent the official views of the Rural Utilities Service. Additional funding provided by U.S. Department of Health and Human Services and revised by RCAC (August 2005) based on materials developed by the Washington State Department of Health, Training and Outreach Section, Division of Drinking Water. For additional copies of this publication, call 888/321-7227or visit RCAP's web site at www.rcap.org. This publication is being distributed under the auspices of Rural Community Assistance Partnership.

- Contents

- Introduction PAGEREF _ 2 HYPERLINK \l "_Toc111350975"

- How to use the template PAGEREF _Toc111350975

- \h 2 HYPERLINK \l "_Toc111350976"

- The requirement for an emergency response plan PAGEREF _Toc111350976 \h 2 HYPERLINK \l "_Toc111350977"

- Section 1. System Information PAGEREF _Toc111350977 \h 3 HYPERLINK \l "_Toc111350978"

- Section 2. Chain of Command ñ Lines of Authority PAGEREF _Toc111350978 \h 4 HYPERLINK \l "_Toc111350979"

- Section 3. Events that Cause Emergencies PAGEREF _Toc111350979 \h 5 HYPERLINK \l "_Toc111350980"

- Section 4. Emergency Notification PAGEREF _Toc111350980 \h 6 HYPERLINK \l "_Toc111350984"

- Section 5. Effective Communication PAGEREF _Toc111350984 \h 10

- Section 6. Response Actions for Specific Events PAGEREF _Toc111350985 \h 11

- Section 7. Alternative Water Sources PAGEREF _Toc111350986 \h 16

- Section 8. Returning to Normal Operation PAGEREF _Toc111350987 \h 17

- Section 9. Plan Approval PAGEREF _Toc111350988 \h 18

- Section 10. HYPERLINK \l "_Toc111350990"

- Certificate of Completion PAGEREF _Toc111350990 \h 19

- Planning Template

- Introduction

- Preparing an emergency response plan is an essential part of managing a drinking water system. Rural Community Assistance Partnership, Inc has developed this template for public water systems serving 3,300 population or fewer to help them develop such plans.

- How to use the template

- Developing an emergency response plan can take a lot of time and effort. The purpose of this document is to make the job easier and help create a plan that works for your water system. The document is intended for use by any water system and may be modified to fit the specific needs of each system. This document can be used as a starting point based on what is relevant for the type, size, and complexity of the system. The template is just a guide; you may modify it in any way that works for your system - add sections, take them out, or rearrange them if you wish. You may also use a completely different format for your plan if you find one that works better for your system. Since this document may contain sensitive information, do not submit it to USDA/RD and make sure to keep it stored in a safe and secure location. It is recommended you have one copy stored on-site and one off-site to ensure the document is available in the event you are unable to access your offices or facilities. The document is available electronically on the web at: http://www.rcap.org

- The requirement for an emergency response plan: The United States Department of Agriculture, Rural Development (USDA/RD) is requiring that all systems that receive USDA/RD funding must complete a Security Vulnerability Assessment (SVA) and Emergency Response Plan (ERP). In addition to the USDA/RD requirements, the preparation of a SVA and ERP will help improve the management of the water system and will increase the system's ability to respond to emergencies. This guidance document can be used to help meet the requirement for developing an emergency response program for a water system serving 3,300 population or fewer. Other methods or formats can also be used to meet the emergency response program requirement.

- Section 1.

- System Information  	Keep this basic information easily accessible to authorized staff for emergency responders, repair people, and the news media.

- System information

- System Identification Number	Public Water System PWS# 0270021

- System Name and Address	Silver Creek Village Water Supply Corporation

- 205 Loma Vista Dr.

- Burnet, TX 78611

- Directions to the System 		From thev City of Burnet, go west on Hwy 29 West. Turn North on Hwy 2341 to CR 128. Turn left (west) on 128. Then turn North (right) on McKay Rd. System located across from Chula Vista Dr. intersecting McKay.

- Basic Description and Location of System Facilities Drinking Water System

- Well #1- house located at CR 128 and South Beach Dr.

- Well #2- inactive, and capped.

- Wells 3 & 4 dry tests.

- Well #5 within fenced treatment and storage area.

- Well #6 - inactive and capped.  At fenced treatment/storage area at McKay & Chula Vista:

- Treatment = Gas chlorination.

- Aeration/Filter 		(Gravel, Sand, Anthracite Coal)

- Ground storage tank, 	65,000 gal.

- Pressure Tank. Location/Town Silver Creek Village, on North East Lake Buchanan in County of Burnet

- Population Served and Service Connections from Division of Drinking Water Records 276 population - TCEQ 		103 connections - TCEQ

- System Owner 	Silver Creek Village Water Supply Corporation

- Name, Title, and Phone Number of Person Responsible for Maintaining and Implementing the Emergency Plan

- Clint Cagle Vice President, SCVWSC Board of Directors (512) 970-6716 Cell

- Section 2.

- Chain of Command 	Lines of Authority

- The first response step in any emergency is to inform the person at the top of this list, who is responsible for managing the emergency and making key decisions.

- Chain of command 	Lines of authority

- Name and Title	Responsibilities During an Emergency	Contact Numbers

- Joey Krueger Water System Operator (512) 755-5680 Cell (512) 756-1042 Home

- Assess emergency.  Make any Water Utility emergency repairs.  Call TCEQ within 24 hours if required.

- Clint Cagle, Vice President, Board of Directors (512) 970-6716 Cell   Assist Operator Joey Krueger in addressing emergency.

- William Cain Board President wecain@sbcglobal.net 4831 Bayou St. John, Conroe, TX

- Paul M. Miller 	Secretary Treasurer 	(512) 923-0883

- Craig Watson 	Board Director 		(719) 931-9029

- Christine Whitelaw Board Director 		(502) 588-2274

- Nelson Brock 	Business Manager 	(512) 756-2450

- Section 3.

- Events that Cause Emergencies

- The events listed below may cause water system emergencies. They are arranged from highest to lowest probable risk.

- Events that cause emergencies

- Type of Event 	Probability or Risk (High-Med-Low) 		Comments

- Power Outage 	Medium Occur infrequently. StandBy Generator for Well #1 pump, Generator for main pump house on order.

- Drought 		Medium   Wells have produced sufficiently, even during drought.

- Line Breaks 	Low   Distribution system lines replaced in 2004. Most breaks are between meter and house and the responsibility of owner. Occasional drive over meter box.

- Equipment Failure 	Low

- Tornado 			Low

- Section 4.

- Emergency Notification call-up lists - Use these lists to notify first responders of an emergency.

- Emergency Notification List

- Organization or Department		Name & Position	Telephone	Night or Cell Phone		Email

- Local Law Enforcement		Burnet County Sheriff 	911 	(512) 756-8080

- Fire Department 			Silver Creek Village VFD 911

- 911 Emergency Medical Services 	Burnet Co. EMS 	911

- 911 Water Operator 		Joey Krueger 	512-755-5680 Cell

- Primacy Agency Contact 	TCEQ Austin 	512-239-1000

- Hazmat Hotline 			Burnet County Sheriff 	911

- Interconnected Water System 	None

- Neighboring Water System (not connected) Jones Owens Water System (serves Silver Creek Village - South)

- RCAP Contact 		Mark Pearson 	512-454-1033 479-445-3724

- Rural Water Contact 	TRWA  		512-472-8591

- Priority Customers Organization or Department

- Name & Position 		Telephone Night or Cell Phone 	Email

- Hospitals or Clinic(s) 		N/A

- Public or Private Schools 	N/A

- Wastewater Treatment Plant 	N/A

- Adult Care Facility 		N/A

- State or Federal Notification List 	Organization or DepartmentName & PositionTelephone		Night or Cell Phone	Email

- State Police 				DPS 		911

- Regulatory Agency State/Federal

- TCEQ Public Drinking Water 	512-239-4691

- Authorized Testing Laboratory

- Drinking Water (bacteriological): Round Rock Lab TCEQ in Austin (Usually delivered by Joey Krueger to the lab) 	512-239-1000

- Service / Repair Notifications

- Organization or Department		Name & Position

- Telephone	Night or Cell Phone	Email

- Electric Utility Co. 	PEC, Pedernales Electric Coop. 512 355-2131 1-888-554-4732

- Electrician 			Hoover Construction   Burnet, TX 	512-756-6041/2139

- Gas/Propane Supplier 	Propane +   		512 756-4927

- Water Testing Lab. TCEQ  512-239-1000

- Sewer Utility Co. N/A

- Telephone Co. Verizon Southwest 512-756-7640

- Plumber 	Brandberg Plumbing 512 756-9847 Greg Hall & Sons 512-755-3679

- Pump Supplier Hoover Const. 800-299-8909 512 756-6041 fax 512 756-7411

- Call Before You Dig 1-800 Dig-Tess	800-344-8377

- Rental Equipment Supplier Minuteman Rentals 512-756-4469 512-755-0297

- Chlorine Supplier Lone Star Maintenance 254-857-4711 800 234-0214

- Well Drilling Co. Western Water Wells 866 756-4077 512-756-4077 Apex 830 798-2739 Pipe Supplier Hoover Const. for line breaks 800-299-8909

- Media Notification List

- Organization or Department Name & Position Night or Cell Phone Email

- Newspaper

- -Local   Burnet Bulletin -weekly Newspaper

- -Regional/State 	Austin American Statesman

- Radio Radio TV Station 		KVUE TV Station-Austin

- Notification procedures Notify water system customers of potential water shortage

- Who is Responsible: Joey Krueger, Operator, determines need to notify customers. (Clint Cagle, as backup)

- Procedures: Calling customer lists and by word of mouth. Assisted by Business Manager and Board Members. Public posting at community center could use Marquee sign. Alert local law enforcement, state, or federal drinking water officials, and local health agencies

- Who is Responsible: Joey Krueger, WSO, Clint Cagle, Board Vice President.

- Procedures: Call to notify if needed. Contact service and repair contractors

- Who is Responsible: Joey Krueger, Operator.

- Procedures:	Calls contractors, notify board. Contact neighboring water systems, if necessary

- Who is Responsible: 	Board Member.

- Procedures: 			Contact as needed.

- Procedures for issuing a health advisory

- Who is Responsible: Joey Krueger will determine need to issue Boil Water Notice. Nelson Brock, business manager, and Board Members will assist to notify customers. Procedures: 		Post notice at Community Center. Use customer call lists and go door to door. Other procedures as necessary

- Who is Responsible:

- Joey Krueger, Clint Cagle, Nelson Brock, other Board Members.

- Procedures:

- Section 5.

- Effective Communication

- Communication with customers, the news media, and the general public is a critical part of emergency response.

- Designated public spokesperson 	Designate a spokesperson (and alternate) and contact your local primacy agency for delivering messages to the news media and the public.

- Designate a spokesperson and alternate

- Spokesperson - Butch Cain 	Board President

- Alternate - Clint Cagle, 		Board Vice President

- Paul M. Miller, 	Board Secretary-Treasurer

- Health advisories

- During events when water quality and human health are in question, it may be necessary to issue a health advisory that gives advice or recommendations to water system customers on how to protect their health when drinking water is considered unsafe. These advisories are issued when the health risks to the consumers are sufficient, in the estimation of the water system, state or tribal, or local health officials, to warrant such advice. Health advisories usually take the form of a drinking water warning or boil water advisory. Communication during these times is critical. Health advisories should always be well thought out and provide very clear messages. The U.S. Environmental Protection Agency has put together a number of tools, including fact sheets, brochures, forms, and templates to help prepare for a health advisory. These are on the web at: HYPERLINK 	"http://www.epa.gov/safewater"

- http://www.epa.gov/safewater /pn.html

- Section 6.

- Response Actions for Specific Events

- In any event, there are a series of general steps to take: Analyze the type and severity of the emergency; Take immediate actions to save lives; Take action to reduce injuries and system damage; Make repairs based on priority demand, and Return the system to normal operation. The following tables identify the assessment, set forth immediate response actions, define what notifications need to be made, and describe important follow-up actions.

- Power outage

- Assessment		Joey Krueger, Clint Cagle.

- Immediate Actions		Check source of power outage: Check breakers. Within System Grounds or Exterior from Power Company transmission lines.

- Notifications	For power outage - call Pedernales Electric Coop, Inc.

- Follow-up Actions		If power down long enough to lose water pressure, then follow normal procedures for loss of water pressure: Boil Water Notice, Flushing, Sampling.

- Distribution line break

- Assessment		Joey Krueger, Clint Cagle.

- Immediate Actions 	Assess extent of break of WSC or customer line. May need to flush line after repair.

- Notifications 	Notify contractor to repair distribution break. Customer is responsible on their side of meter. Only if loss of pressure. Then issue Boil Water Notice procedure.

- Follow-up Actions		If loss of pressure, then do bacteriological sampling.

- Chlorine treatment equipment failure

- Assessment		Joey Krueger. Clint Cagle, as backup. Check chlorine residuals.

- Immediate Actions - 2 people required to check chlorine, change tank, or repair lines.

- One person goes in chlorine room. 2nd person stays outside with oxygen breathing apparatus for rescue of person in chlorine room if required. Check if tank is empty, check connections, check for broken lines.

- Notifications	If residuals low or non-existent, then issue Boil Water Notice.

- Follow-up Actions		Check chlorine residuals after repair.

- Treatment equipment 	(Aeration and Filters)

- Assessment 		Joey Krueger. Clint Cagle, as backup, or other resident board member.  In past filter material was mineralized by hard water which slowed down water flow, required replacing filter material (Replaced in 2022). Aeration is to remove odors, followed by gravel, sand, charcoal.

- Immediate Actions 	Repair as needed.

- Notifications 	Notify customers and TCEQ for any Drinking Water Treatment failure.

- Follow-up Actions

- Source pump failure

- Assessment 		Joey Krueger. Clint Cagle, as backup, or other resident board member. For Groundwater Well pump. Immediate Actions - Determine if it is the well not pumping, Call Western Water Well if needed.

- Notifications 	None required, if there is enough water in the Storage Tank to supply membership until well pump is repaired.

- Follow-up Actions 	None

- Microbial (coliform, E. coli) contamination

- Assessment 		Positive Bacteriological test result.

- Immediate Actions 	Flush lines. Repeat with 3 samples. Send back to Lab to test. Notifications 	If repeat sample is positive, issue Boil Water Notice. Use customer call list.

- Follow-up Actions 	When repeat sample/test is negative, withdraw Boil Water Notice. If repeat sample is still positive. Retest with 5 samples. Notify TCEQ.

- Chemical contamination

- Assessment 		Possibly show up as loss of chlorine residual, other taste or odor problem. Or causing health problems. Possibly noticed due to affecting multiple customers.

- Immediate Actions 	If extreme concern, shut off storage tank. Shut down pumps. Take sample to Lab.

- Notifications 		Call TCEQ to sample and test water. Notify customers.

- Follow-up Actions 	As required by state/TCEQ.

- Reduction or loss of water in the well

- Assessment		Call Western Water Wells to assess pump or water level issue.

- Immediate Actions 	As advised by Western Wells

- Notifications 		As required

- Follow-up Actions 	As required

- Vandalism or terrorist attack 		Assessment

- Call Sheriff Dept. 		Assess any needed changes to protect customers.

- Immediate Actions 	Assess water system.

- Notifications 		As required

- Follow-up Actions 	As required

- Drought Assessment

- Water System has not been affected by recent drought in the area.

- Immediate Actions 	Follow Drought Contingency Plan.

- Notifications 		As required

- Follow-up Actions 	As required

- Flood Assessment

- No flooding concerns. Water facilities on high hill above lake.

- Immediate Actions 	As required

- Notifications 		As required

- Follow-up Actions 	As required

- Hazardous materials spill in vicinity of sources or system lines

- Assessment 		Hazardous Spills not likely in area. Call 911 and Fire Dept.

- Immediate Actions 	Block off area. Try to isolate any affected water lines, especially if pressure lost.

- Notifications 	TCEQ SPILL REPORTING LINE: 1-800-832-8224 (At night answered as State Emergency Response Commission.)

- Follow-up Actions 	As required

- Electronic equipment failure

- Assessment 		Joey Krueger.  Clint Cagle, as backup

- Some automated control panels for cut-on and off: Well pump, aerator pump, transfer pump, booster pumps, compressor for pressure tank.

- Immediate Actions 	For electrical repairs call electrician or Hoover Construction and tell the nature of problem.

- Notifications 	Depends on nature of failure. Contact TCEQ or customers as required.

- Follow-up Actions 	As required

- Cyber attack/Computer failure

- Assessment 		No computer controls to water system.

- Immediate Actions 	Important computer files such as billing records, etc. are backed up to disk regularly and stored in a separate and/or fireproof location.

- Notifications 		As required

- Follow-up Actions 	As required

- Other Assessment 	N/A

- Immediate Actions

- Notifications

- Follow-up Actions

- Section 7.

- Alternative Water Sources

- Intertie [an interconnection permitting passage of current between two or more electric utility systems] to adjacent water supply system

- Water Systems Within One-Quarter Mile of our System 		Feasibility of Connecting Owens Jones Water Company 		Might be feasible.

- Completing Surface Water Treatment Plant will provide alternate water source. Feasible. In progress.

- Alternate source(s) of water

- Alternative Sources

- Names 	Phone 	Availability

- Is the Water Safe for Drinking?

- Bottled water Suppliers for potable water use

- Silver Creek One-Stop Convenience store.

- HEB in Burnet.

- Walmart in Marble Falls.

- Tanker trucks in the area available to deliver bulk water for non potable use

- Contact TCEQ Drought Coordinator for referral.512-239-1000

- Section 8.

- Returning to Normal Operation

- Returning to normal operations

- Action Description and Actions

- Restore Power. All Switches On.

- Turn on Chlorine.

- Correct Settings.

- Take bacteriological samples and send to Lab.

- Section 9.

- Plan Approval 	This plan is officially in effect when reviewed, approved, and signed by the following people:

- Name/Title 		Signature 		Date

- William Cain, Board President

- Clint Cagle, Vice President

- Joey Krueger, Operator

- Section 10.

- Certificate of Completion

- I certify to the United States Department of Agriculture, Rural Development (USDA/RD) that this community water system has completed an Emergency Response Plan (ERP) that incorporates the results of the Security Vulnerability Assessment (SVA) completed for the system.

- I certify that this document was prepared under my direction or supervision. I am aware that there are significant penalties for submitting false information (Safe Drinking Water Act (42U.S.C. 300f et seq.).

- Mail the completed certificate only (do not send your SVA or ERP) to the appropriate USDA Rural Development office.

- Public Water System ID Number: PWS #0270021

- System Name: Silver Creek Village WSC

- Address: 205 Loma Vista Drive, Burnet, TX 78611

- Print Name of Person Authorized to Sign this Certification on behalf of the System: Clint Cagle

- Title:Vice President, Silver Creek Village WSC Board of Directors

- Signature:

- Phone:512-970-6916

- Fax:

- Email: clintcagle@gmail.com

- Received Technical Assistance from the following:

- x Rural Community Assistance Partnership (CRG, Great Lakes RCAP/WSOS, MAP, RCAC, RCAP Solutions, Southeast RCAP) Rural Water Association

- Completing the following:

- x Security Vulnerability Assessment x Emergency Response Plan Rual Community Assistance Partnership, Inc. 1522 K Street, N.W., Suite 400 Washington, D.C. 20005 888/321-7227

- PAGE 2

- Emergency Response Planning Guide for Public Drinking Water Systems Emergency Response Planning Template for Public Drinking Water Systems

- PAGE 20 Disclaimer

- This document contains information on how to plan for protection of the assets of your water system.

- The work necessarily addresses problems in a general nature.

- You should review local, state, tribal (if applicable), and federal laws and regulations to see how they apply to your specific situation.

- Knowledgeable professionals prepared this document using current information.

- The authors make no representation, expressed or implied, that this information is suitable for any specific situation. The authors have no obligation to update this work or to make notification of any changes in statutes, regulations, information, or programs described in this document.

- Publication of this document does not replace the duty of water systems to warn and properly train their employees and others concerning health and safety risks and necessary precautions at their water systems.

- Rural Community Assistance Partnership, Inc. assumes no liability resulting from the use or reliance upon any information, guidance, suggestions, conclusions, or opinions contained in this document.

- Northeast RCAP

- Southeast RCAP

- RCAP National Office

- Southern RCAP

- Great Lakes RCAP

- Midwest RCAP

- Western RCAP